## Introduction
1. This file includes parameters of microgrid EMS for resilience services, CLPU models used for the manuscript: " Modeling Cold Load Pickup in Energy Management for Resilience Services in Distribution Systems" 2. Input data (PV, load, temperature, circuit, HVAC ss-RCQ* model parameters) can be found in conresponding input folders 3. Location and periods of temperature, PV, load data: Austin, Texas, August 1-25, 2017
*Du P, Lu N, Zhong H. Demand response in smart grids. Cham: Springer International Publishing; 2019 Jul 2.

## Microgrid_EMS
Microgrid components & their operation
PV (3-ph) | 1,500 kW per ph
BESS power rate (3-ph) | 1,000 kW per ph
BESS energy rate | 6,000 kWh
BESS charging and discharging efficiency | 0.95
BESS SOC operational region | [0.2, 0.9]
BESS initial SOC | 0.9
EMS
interval | delta t | 1h
optimization horizon | T | 48h
preferred supply periods |  | 7:00-9:00 | 18:00-20:00
weighting for load serving during preferred periods | w | 1.5
PV curtailment penalty coefficient | c^(pv) | 0.0001
system reserve (% of served load) |  | 15%
M for the big-M method | M | 48

## CLPU models
Models | Parameters
NoCLPU | No
FixCLPU | CLPU addition | Pclpu | the normal load, i.e. the load forecst
| CLPU duration | Dclpu | 1 hour
AepCLPU | CLPU consumption ratio | k^(CLPU) | calculated based on identified HVAC rating and HVAC load at the conresponding temperature from smart meter data
| CLPU duration | Dclpu | 1 h when the temperature of restoring load <= 32 C, 2 h when temperature > 32 C
AdaptCLPU |  | the total rating of all HVACs | the total normal load of all HVACs | The peak duration rate | the peak duration saturation | The decay rate | The introduction of this model can be found in the paper: Adaptive cold-load pickup considerations in 2-stage microgrid unit commitment for enhancing microgrid resilience (https://www.sciencedirect.com/science/article/abs/pii/S0306261923017889)
| temperature (°C) | Ppeak (kW) | Pnorm (kW) | peak_dura_rate (hour/ hourly outage period ) | peak_dura_satu (hour) | decay_dura (p.u./ hourly supply period ) | p.u. : normalized power based on the total rating of all HVACs
|  | P^(MaxHVAC) | P^(steady) | tau^(Tout) | d^(peaksatu) | gamma^(Tout) | Please note that parameters' values should be scaled based on the intervals you selected
| 24 | 3173 | 330.5755 | 0.075 | 0.2 | 2.0579
| 25 | 3173 | 510.1901 | 0.0875 | 0.35 | 1.5908
| 26 | 3173 | 695.685 | 0.12917 | 0.51667 | 1.3162
| 27 | 3173 | 859.6422 | 0.175 | 0.7 | 1.0822
| 28 | 3173 | 1068.3528 | 0.22083 | 0.88333 | 0.8712
| 29 | 3173 | 1229.2808 | 0.27083 | 1.0833 | 0.683
| 30 | 3173 | 1420.6269 | 0.325 | 1.3 | 0.55
| 31 | 3173 | 1602.5966 | 0.38333 | 1.5333 | 0.41
| 32 | 3173 | 1788.176 | 0.45 | 1.8 | 0.31
| 33 | 3173 | 1960.0463 | 0.51667 | 2.0667 | 0.22
| 34 | 3173 | 2144.8775 | 0.59167 | 2.3667 | 0.15099
| 35 | 3173 | 2325.978 | 0.67083 | 2.6833 | 0.11112
| 36 | 3173 | 2504.9246 | 0.8 | 3.0667 | 0.076828
| 37 | 3173 | 2702.6224 | 0.9 | 3.45 | 0.051115
| 38 | 3173 | 2844.7178 | 1.0609 | 4.0667 | 0.034006
| 39 | 3173 | 2956.573 | 1.48 | 4.9333 | 0.020987
| 40 | 3173 | 3043.8331 | 1.83 | 6.1 | 0.010803